## AF
Design of Anaerobic Filter (AF) | [6 empty] | Design Procedure
Description | Symbol | Value | Unit | Description | Calculation | Unit | Description | Formula/Design Steps
Given Parameters |  |  |  | Calculation |  |  | Calculation
Daily Wastewater Flow | Q | 10 | m3/d | Assume, Liquid depth at outlet, H = | 1.8 | m | Assume H = | This equals liquid depth of ABR at outlet
Number of unit | N | 1 | nos. | Assume, Length of AF, L = | 1 | m | Assume L = | Length of filter chamber ≤ depth of filter chamber
Design wastewater flow | Qd | 10 | m3/d | Assume, breadth of AF, B = | 3 | m | Assume B = | Assume
Peak Hours | tP | 2 | hr | Number of Filter Chamber, Nc = | 2 | nos | Nc = | Take number of unit 1-3
Peak flow | QP | 5 | m3/h | Thickness of Slab, d = | 0.05 | m | d = | Take as per design or requirement
Influent BOD | BODin | 179 | mg/L | Thickness of Filter media, D = | 0.75 | m | D = | H-Upper freeboard-Lower freeboard - Thickness of slab
Influent COD | CODin | 541 | mg/L | Max Velocity in filter media, VUP = | 3.7037 | m/h | VUP = | Qp/(L*B*Void%)
Lowest temperature | T | 20 | oC | Check for velocity in filter media |  |  | Check for velocity in filter media
Specific Surface area of Filter media | Asf | 120 | m2/m3 |  | recheck |  | Maximum Upflow velocity should be 2 m/h
Voids in Filter media (30%-45%) | Void | 45% |  | Calculate Vol. of AF |  |  | Calculate Vol. of AF
Chosen Parameters |  |  |  | Volume of AF, V = | 8.325 | cum | V = | Nc*L*B*(L-D*(1-Void%))
Up Flow Velocity (0.9 to 2 m/h) | VUP | 0.9 | m/h | Check for COD loading and HRT |  |  | Check for COD loading and HRT
Upper free board | HUFB | 0.4 | m | COD loading = | 0.64985 | kg/m3d | COD loading = | Qd*CODin/V/1000
Lower free board | HLFB | 0.6 | m |  | OK |  | Organic loading should be < 4 kg/m3/day COD
|  |  |  | HRT in Filter tHRT = | 20 | hrs | tHRT = | ((H-D*(1-0.4))*L*B*Nc)/(Qd/24)
Summary of AF size |  |  |  | Is theAF is stand-alone treatment unit? | No |  | Hydraulic Retention Time, tHRT should be 15-20 hours in DEWATS and 24-48 hours in stand-alone treatment
Length of chamber | L | 1 | m |  | OK
Width or Breadth | B | 3 | m | Calculate BOD and COD of effluent |  |  | Calculate BOD and COD of effluent
Water Depth | H | 1.8 | m | factor strength, ƒS = | 0.91599 |  | ƒS = | a (Use graph for Factor fS)
Thickness of Filter media | D | 0.75 | m | factor temperature, ƒT = | 0.86 |  | ƒT = | b (Use graph for Factor fT)
BOD of effluent | BODout | 71.779 | mg/L | factor Organic Load, ƒO = | 1 |  | ƒO = | c (Use graph for Factor fO)
COD of effluent | CODout | 239.7904 | mg/L | factor HRT, ƒHRT = | 0.64667 |  | ƒHRT = | d (Use graph for Factor fHRT)
Size of filter media (Gravel or Cinder) |  | 80-140 | mm | factor Chamber, ƒN = | 1.08 |  | ƒN = | e (Use graph for Factor fN)
|  |  |  | factor surface, ƒsur = | 1.012 |  | ƒsur = | f (Use graph for Factor fsur)
|  |  |  | COD removal by factor, CODrem.rate = | 55.68% |  | CODrem.rate = | a * b * c * d * e * f
|  |  |  | Applied COD removal rate = | 55.68% |  | CODrem.rate = | IF(K29<0.8,K29,IF((K29*(1-0.37*(K29-0.8)))<0.95,K29*(1-0.37*(K29-0.8)),0.95))
|  |  |  | COD of effluent, CODout = | 239.7904 | mg/ltrs | CODout = | (1-BODrem.rate)*BODin
|  |  |  | Factor Efficiency of BODrem to CODrem, fBODtoCOD = | 1.0748 |  | fBODtoCOD = | x (Use graph for Factor fBODtoCOD)
|  |  |  | BOD removal rate, BODrem rate = | 59.9% |  | BODrem rate = | fBODtoBOD*BODrem.rate
|  |  |  | BOD of effluent, BODout = | 71.779 | mg/ltrs | BODout = | (1-CODrem.rate)*CODin

## Graph AF
Graph for Factor fS
Graph for Factor fT
Graph for Factor fO
Graph for Factor fHRT
Graph for Factor fN
Graph for Factor fsur
Graph for Factor fBODtoCOD