KTP FSTP DRAINAGE LAYOUT

Brief

UNHCR -OXFAM and MSF is constructing a Centralized Fecal Sludge Treatment Plant with 180 m3 capacity / day. For effective storm water drainage and final effluent discharge, this plant  need a proper drainage system. Below sections are documented for explaining the drainage layout and requirement to use the existing drain of DRC compound  jointly for the site.

Figure 1: Proposed Route for surface drainage at KTP FSTP

Following The design calculation, total area has been divided into following three section of drains

Figure 2: Different Cross section of drains , Inside the DRC compound drain section will follow the existing excavated portion

Figure 3: Layout of Type A , B and C drain

Accessing DRC Compound

The natural contour and drainage is going through the DRC compound where there is existing earther drain ( Figure )

UNHCR and OXFAM team did a visit to the site on 20th June ,2021 and had a discussion with the responsible DRC person. Initially they have mentioned that, there is no plan to do civil construction work at the existing drain inside DRC compound.

OXFAM proposition

- OXFAM will do the civil construction work of the drain inside the DRC compound following current drain route.

- All the surface runoff of KTP FSTP catchment and final effluent of the FSTP to be connected with this drain.

- OXFAM will construct cover slab for the drains inside the DRC site as per requirement.

ANNEX - Drainage Design Calculation

Surface of the terrain / determination of runoff coefficient –

Runoff coefficient of .6 was selected as forest and pastures with gradient >.05

Determination of rainfall intensity

As no local IDF ( Intensity -Duration – Frequency curve was not available.

MAX rainfall intensity of 200mm/ Hr has been calculated for Kutupalong , Ukhiya.

Amount of water the catchment will produce –

Qdesign = 2.8XCXiXA

Qdesign= The design peak runoff rate, or the maximum flow of storm water the system will be designed for ( In litres per second )

C= The runoff coefficient

I = The rainfall intensity at the time of concentration read from the chosen IDF curve / Average value in mm/h

A= The surface area of the catchment area in ha

Drain Sizing

Q= 1000 X ( A X (R).67 X (S).5 / N)

Q= The capacity of discharge of the drain  ( l/s )

A= The cross section of the flow ( in m2 )

R = The hydraulic radius of the drain ( Cross sectional area / Total length of contact between water and drain )

S= The gradient of the drain

N = Manning’s roughness coefficient ( for brick drain .025 ) – Check )

Take 20% Safety Factor ( For solid deposition , Satellite variation , lack of maintenance etc.

|  | Width | Height | Area | R^.67 | S^.5 | Q trialed |
| --- | --- | --- | --- | --- | --- | --- |
| C | 0.7 | 0.5 | 0.35 | 0.346837 | 0.125656 | 610.1501 |
| B | 0.6 | 0.4 | 0.24 | 0.306786 | 0.125656 | 370.0759 |
| A | 0.5 | 0.3 | 0.15 | 0.263177 | 0.125656 | 198.4189 |

|  |  | L/s |  |  |  |  |  | L/s |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Area | Size( Ha ) | Q designed | W | H | A | R^.67 | S^.5 | Q trialed |
| A | 0.43 | 144.48 | 0.6 | 0.6 | 0.36 | 0.340165 | 0.125656 | 615.5118 |
| B | 0.43 | 144.48 | 0.6 | 0.6 | 0.36 | 0.340165 | 0.125656 | 615.5118 |
| C | 0.47 | 157.92 | 0.6 | 0.6 | 0.36 | 0.340165 | 0.125656 | 615.5118 |
| D | 0.21 | 70.56 | 0.6 | 0.6 | 0.36 | 0.340165 | 0.125656 | 615.5118 |
| E | 0.22 | 73.92 | 0.6 | 0.6 | 0.36 | 0.340165 | 0.125656 | 615.5118 |
| F | 0.19 | 63.84 | 0.6 | 0.6 | 0.36 | 0.340165 | 0.125656 | 615.5118 |
| G | 0.11 | 36.96 | 0.6 | 0.6 | 0.36 | 0.340165 | 0.125656 | 615.5118 |
| H | 0.12 | 40.32 | 0.6 | 0.6 | 0.36 | 0.340165 | 0.125656 | 615.5118 |
| I | 0.65 | 218.4 | 0.6 | 0.6 | 0.36 | 0.340165 | 0.125656 | 615.5118 |
| J | 0.52 | 174.72 | 0.6 | 0.6 | 0.36 | 0.340165 | 0.125656 | 615.5118 |
| K | 0.12 | 40.32 | 0.6 | 0.6 | 0.36 | 0.340165 | 0.125656 | 615.5118 |
| L | 0.14 | 47.04 | 0.6 | 0.6 | 0.36 | 0.340165 | 0.125656 | 615.5118 |
| M | 0.57 | 191.52 | 0.6 | 0.6 | 0.36 | 0.340165 | 0.125656 | 615.5118 |
|  | 4.18 | 1404.48 |  |  |  |  |  |  |